## FLEX-TAPE
COMPLIANCE STATEMENT
Item Type: LED Strip — Soft Cove, 3000K, CRI≥90, ~2000 lm/m, 24V DC [tuned]
PROJECT: LightSelect Demo Project ¦ DATE: 22 Jun 2026
LIGHTING CONSULTANT: AECOM ¦ REF: LS-2026-001 REV. Rev A
GENERAL DESCRIPTION
Description | Surface-mounted flexible LED tape for soft cove/perimeter lighting. Indoor (IP≥20). White output only (colour channels disqualified). 3000K ±100K absolute. CRI≥90. ~2000 lm/m delivered.
LUMINAIRE (FIXTURE)
Parameter | Specified | Proposed | Comments / Compliance
Manufacturer | — | EXAMPLE
Manufacturer Product Reference | — | OPAL-EXAMPLE
IP Rating | ≥ IP20 | IP20 | Comply
IK Rating | — | —
Mounting Type | — | —
Body Material | — | —
Reflector Material | — | —
Body Colour | — | —
Country of Origin | — | —
Operating Temperature | — | —
Physical Dimensions | — | 600x0.5x0.2 cm
Accessories | — | —
LAMP / SOURCE
Parameter | Specified | Proposed | Comments / Compliance
Manufacturer | — | ILTI LUCE
Reference | — | 1-WKL-6023-0-00
Type | — | —
Beam Angle | — | 120°
Voltage | 24V DC | 24V DC | Comply
Wattage | ≤ 20 W/m | 14.4 | Comply
SDCM | — | —
CRI | ≥ 90 | 90 | Comply
Colour Temperature | 3000 K | 3000 | Comply
Lumen Output (DELIVERED) | ~2000 lm/m | 1184 lm/m | Deviation – undershoot 26.0% exceeds −10% limit. Delivered = source × 80% (estimated transmission (placeholder — verify before issue))
CONTROL GEAR / BALLAST / TRANSFORMER
Parameter | Specified | Proposed | Comments / Compliance
Type | — | —
Manufacturer | — | —
Reference | — | —
Other